## Version Information
illustrate | state | Function code | Address - decimal
Version number: 16 characters | Read-only integer | 0X04 | 256

## User operation commands
illustrate | state | Function code | Point Name | Address - decimal
0XFF00: Power on | Write only switch quantity | 0X05 | Unit startup | 0
0XFF00: Shutdown |  |  | Unit shutdown | 1
0XFF00: Reset |  |  | Reset Command | 8
0XFF00: Silence |  |  | Mute command | 9
0XFF00: n# module defrost |  |  | Manual defrost | 16+n
| Modbus Address | Setting range | default value | unit
Control Mode | 6400 | 1…6 | 2 | / | {"1":"Constant temperature mode","2":"Cooling mode","3":"Heating mode","4":"Hot water mode","5":"Hot water & cooling mode","6":"Hot water & heating mode"}
Refrigeration set temperature | 6401 | min…max | 12 | ℃ | min: [lower limit of cooling setting], max: [upper limit of cooling setting]
Heating set temperature | 6402 | min…max | 45 | ℃ | min: [lower limit of heating setting], max: [upper limit of heating setting]
Hot water setting temperature | 6403 | 30…60 | 50 | ℃
Power Mode | 6405 | 0…2 | 0 | / | {"0":"Standard","1":"Powerful","2":"Energy-saving"}
Silent Mode | 6406 | 0…2 | 0 | / | {"0":"Disable","1":"Mute at night","2":"Mute all day"}
Night silence on | 6407 | 0…23 | 22 | h
Nighttime silent opening | 6408 | 0…59 | 0 | m
Night silent off | 6409 | 0…23 | 7 | h
Nighttime silent mode | 6410 | 0…59 | 0 | m
Duty function enabled | 6411 | 0…1 | 0 | / | {"0":"Disable","1":"Enable"}
Heating duty temperature | 6412 | min…max | 0 | ℃ | min: [lower limit of heating setting], max: [upper limit of heating setting]
Refrigeration duty temperature | 6413 | min…max | 0 | ℃ | min: [lower limit of cooling setting], max: [upper limit of cooling setting]
Duty time | 6414 | 0…23 | 0 | h
Duty activation segment | 6415 | 0…59 | 0 | m
Duty downtime | 6416 | 0…23 | 0 | h
Duty suspension period | 6417 | 0…59 | 0 | m
Heating two-way interlock | 6418 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
Pump operation mode | 6421 | 0…2 | 0 | / | {"0":"Run continuously","1":"Stop when temperature reaches","2":"Run intermittently"}
Terminal pump enable | 6422 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
Number of modules | 6430 | 1…8 | 1 | /
00#Module Settings | 6431 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
01#Module Settings | 6432 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
02#Module Settings | 6433 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
03#Module Settings | 6434 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
04#Module Settings | 6435 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
05#Module Settings | 6436 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
06#Module Settings | 6437 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}
07#Module Settings | 6438 | 0…1 | 1 | / | {"0":"Disable","1":"Enable"}

## Crew information
illustrate | state | Function code | Point Name | Address - decimal
B0: Unit standby state B1: Unit starting B2: Unit running state B3: Unit stopping B4: Unit serious alarm state B5: B6: B7: B8: Unit preheating B9: Unit fault B10: Unit antifreeze B11: Unit defrosting B12: B13: B14: B15: Two-way valve interlock | Read-only integer | 0X04 | Unit status | 768
|  |  | Number of presses | 769
Please refer to "Mode Setting" in the parameter table. |  |  | Setting mode | 770
Please refer to "Mode Setting" in the parameter table. |  |  | Current operating mode | 771
Unit 0.1℃ |  |  | Air conditioning set temperature | 772
Unit 0.1℃ |  |  | Air conditioning temperature control | 773
B0:0# Module usage disabled B1:1#Module usage disable B2:2#Module usage disable B3:3#Module usage disable B4:4#Module usage disable B5:5#Module usage disable B6:6#Module usage disable B7:7# Module usage disabled B8: B9: B10: B11: B12: B13: B14: B15: |  |  | Module Usage | 788
Unit: Hour |  |  | System running time | 1024
|  |  | Press running time 1 | 1025
|  |  | Press running time 2 | 1026
|  |  | Press running time 3 | 1027
|  |  | Press running time 4 | 1028
|  |  | Press running time 5 | 1029
|  |  | Press running time 6 | 1030
|  |  | Press running time 7 | 1031
|  |  | Press running time 8 | 1032

## Analog
Read-only integer; function code: 04
Module resources |  | Address (decimal) | [7 empty] | System resources |  | Address (decimal)
Point Name | unit | 0#Module | Module 1# | Module 2# | Module 3# | Module 4# | Module 5# | Module 6# | Module 7# | Point Name | unit
Constant frequency current | 0.1A | 1300 | 1556 | 1812 | 2068 | 2324 | 2580 | 2836 | 3092 | Return water temperature | 0.1℃ | 3348
Main electric expansion | step | 1301 | 1557 | 1813 | 2069 | 2325 | 2581 | 2837 | 3093 | Outlet water temperature |  | 3349
Auxiliary electric expansion | step | 1302 | 1558 | 1814 | 2070 | 2326 | 2582 | 2838 | 3094 | Ambient temperature |  | 3350
Fin temperature | 0.1℃ | 1303 | 1559 | 1815 | 2071 | 2327 | 2583 | 2839 | 3095 | Hot water tank temperature |  | 3351
Exhaust temperature |  | 1304 | 1560 | 1816 | 2072 | 2328 | 2584 | 2840 | 3096
Suction temperature |  | 1305 | 1561 | 1817 | 2073 | 2329 | 2585 | 2841 | 3097
Valve back temperature |  | 1306 | 1562 | 1818 | 2074 | 2330 | 2586 | 2842 | 3098
Top pressing temperature |  | 1307 | 1563 | 1819 | 2075 | 2331 | 2587 | 2843 | 3099
Evaporation saturation temperature |  | 1308 | 1564 | 1820 | 2076 | 2332 | 2588 | 2844 | 3100
Condensation saturation temperature |  | 1309 | 1565 | 1821 | 2077 | 2333 | 2589 | 2845 | 3101
Press low pressure | 0.1bar | 1310 | 1566 | 1822 | 2078 | 2334 | 2590 | 2846 | 3102
Press high pressure | 0.1bar | 1311 | 1567 | 1823 | 2079 | 2335 | 2591 | 2847 | 3103
Main valve target superheat | 0.1℃ | 1312 | 1568 | 1824 | 2080 | 2336 | 2592 | 2848 | 3104
Main valve is currently overheated |  | 1313 | 1569 | 1825 | 2081 | 2337 | 2593 | 2849 | 3105
Auxiliary valve target overheat |  | 1314 | 1570 | 1826 | 2082 | 2338 | 2594 | 2850 | 3106
Auxiliary valve is currently overheated |  | 1315 | 1571 | 1827 | 2083 | 2339 | 2595 | 2851 | 3107
Economizer Import |  | 1316 | 1572 | 1828 | 2084 | 2340 | 2596 | 2852 | 3108
Economizer Export |  | 1317 | 1573 | 1829 | 2085 | 2341 | 2597 | 2853 | 3109
Frost-free operation ring wing difference |  | 1318 | 1574 | 1830 | 2086 | 2342 | 2598 | 2854 | 3110
Target speed of variable frequency compressor | 0.1rps | 1319 | 1575 | 1831 | 2087 | 2343 | 2599 | 2855 | 3111
Current speed of variable frequency compressor | 0.1rps | 1320 | 1576 | 1832 | 2088 | 2344 | 2600 | 2856 | 3112
Frequency converter voltage | 0.1V | 1321 | 1577 | 1833 | 2089 | 2345 | 2601 | 2857 | 3113
Frequency converter current | 0.1A | 1322 | 1578 | 1834 | 2090 | 2346 | 2602 | 2858 | 3114
Inverter temperature | 0.1℃ | 1323 | 1579 | 1835 | 2091 | 2347 | 2603 | 2859 | 3115
Inverter frequency limit information |  | 1324 | 1580 | 1836 | 2092 | 2348 | 2604 | 2860 | 3116
Variable frequency input current | 0.1A | 1325 | 1581 | 1837 | 2093 | 2349 | 2605 | 2861 | 3117
Variable frequency output power | 0.01 | 1326 | 1582 | 1838 | 2094 | 2350 | 2606 | 2862 | 3118
Set fan 1 speed | rpm | 1327 | 1583 | 1839 | 2095 | 2351 | 2607 | 2863 | 3119
Current fan 1 speed | rpm | 1328 | 1584 | 1840 | 2096 | 2352 | 2608 | 2864 | 3120
Set fan 2 speed | rpm | 1329 | 1585 | 1841 | 2097 | 2353 | 2609 | 2865 | 3121
Current fan 2 speed | rpm | 1330 | 1586 | 1842 | 2098 | 2354 | 2610 | 2866 | 3122
EC fan 1 warning information |  | 1331 | 1587 | 1843 | 2099 | 2355 | 2611 | 2867 | 3123
EC fan 2 warning information |  | 1332 | 1588 | 1844 | 2100 | 2356 | 2612 | 2868 | 3124
Condensation return water temperature | 0.1℃ | 1333 | 1589 | 1845 | 2101 | 2357 | 2613 | 2869 | 3125
Condensation water temperature |  | 1334 | 1590 | 1846 | 2102 | 2358 | 2614 | 2870 | 3126
Temperature after refrigeration valve |  | 1335 | 1591 | 1847 | 2103 | 2359 | 2615 | 2871 | 3127
Temperature after heating valve |  | 1336 | 1592 | 1848 | 2104 | 2360 | 2616 | 2872 | 3128
\ |  | 1337 | 1593 | 1849 | 2105 | 2361 | 2617 | 2873 | 3129
\ |  | 1338 | 1594 | 1850 | 2106 | 2362 | 2618 | 2874 | 3130
\ |  | 1339 | 1595 | 1851 | 2107 | 2363 | 2619 | 2875 | 3131
\ |  | 1340 | 1596 | 1852 | 2108 | 2364 | 2620 | 2876 | 3132
\ |  | 1341 | 1597 | 1853 | 2109 | 2365 | 2621 | 2877 | 3133
\ |  | 1342 | 1598 | 1854 | 2110 | 2366 | 2622 | 2878 | 3134
\ |  | 1343 | 1599 | 1855 | 2111 | 2367 | 2623 | 2879 | 3135
\ |  | 1344 | 1600 | 1856 | 2112 | 2368 | 2624 | 2880 | 3136
\ |  | 1345 | 1601 | 1857 | 2113 | 2369 | 2625 | 2881 | 3137
\ |  | 1346 | 1602 | 1858 | 2114 | 2370 | 2626 | 2882 | 3138
\ |  | 1347 | 1603 | 1859 | 2115 | 2371 | 2627 | 2883 | 3139
Module temperature recovery | 0.1℃ | 1348 | 1604 | 1860 | 2116 | 2372 | 2628 | 2884 | 3140
Module output temperature |  | 1349 | 1605 | 1861 | 2117 | 2373 | 2629 | 2885 | 3141
Module ambient temperature |  | 1350 | 1606 | 1862 | 2118 | 2374 | 2630 | 2886 | 3142
Anti-icing temperature |  | 1351 | 1607 | 1863 | 2119 | 2375 | 2631 | 2887 | 3143

## Input, Output
Read-only integer; function code: 04
Point Name | illustrate | Address (decimal) | [7 empty] | Point Name | illustrate | Address (decimal)
|  | 0#Module | Module 1# | Module 2# | Module 3# | Module 4# | Module 5# | Module 6# | Module 7#
Press relay output | B0: Compressor B1: Four-way valve B2: Liquid injection valve B3: Constant frequency fan 1 B4: Constant frequency fan 2 B5: Crankshaft electric heating B6: Enthalpy increase valve B7: Defrost valve | 1283 | 1539 | 1795 | 2051 | 2307 | 2563 | 2819 | 3075 | System relay output | B0: Water tank electric heating B1: Air conditioning pump B2: Electric auxiliary heating B3: Floor heating valve B4: Cooling pump B5: Three-way valve B6: Terminal pump B7: Blower | 3331
Unit relay output | B0: Chassis electric heating B1: B2: B3: B4: B5: B6: B7: | 1285 | 1541 | 1797 | 2053 | 2309 | 2565 | 2821 | 3077
Press switch input | B0: Low voltage switch B1: High voltage switch B2: B3: B4: B5: B6: B7: | 1286 | 1542 | 1798 | 2054 | 2310 | 2566 | 2822 | 3078 | System switch input | B0: Two-way valve interlock B1: Line control switch B2: B3: Air supply pressure difference B4: B5: B6: B7: | 3334
Unit switch input | B0: B1: B2: Water source/fan overload B3: Water flow switch B4: Power failure B5: Frequency reduction switch B6: B7: | 1288 | 1544 | 1800 | 2056 | 2312 | 2568 | 2824 | 3080

## Fault
Read-only integer; function code: 04
Point Name | illustrate | Address (decimal) | [7 empty] | Point Name | illustrate | Address (decimal)
|  | 0#Module | Module 1# | Module 2# | Module 3# | Module 4# | Module 5# | Module 6# | Module 7#
Press failure 1 | B0: Low pressure B1: High pressure B2: Compressor current is too large B3: Compressor current is too small B4: Fin temperature probe failure B5: Exhaust temperature probe failur B6: Exhaust temperature is too high B7: Low pressure sensor failure B8: High pressure sensor failure B9: Low pressure is too low B10: High pressure is too high B11: Suction temperature failure B12: Valve rear temperature failure B13: Refrigeration suction is too low B14: Emergency defrosting is frequent B15: Suction and exhaust temperature difference is frequent | 1294 | 1550 | 1806 | 2062 | 2318 | 2574 | 2830 | 3086 | System Failure 1 | B0: B1: Phase error protection B2: EEPROM data error B3: System ambient temperature failure B4: System temperature return failure B5: System temperature output failure B6: System maintenance data error B7: Phase loss protection B8: Air supply pressure difference | 3342
Press failure 2 | B0: Refrigeration evaporation is too low B1: Frequency reduction switch B2: Standby B3: Return water temperature is too low B4: Return water temperature is too high B5: Fan 1 speed is abnormal B6: Fan 2 speed is abnormal B7: EC1 communication failure B8: EC1 failure B9: EC2 communication failure B10: EC2 failure B11: Frequency conversion communication failure B12: Frequency conversion failure B13: Frequency conversion model is being set B14: Economizer inlet temperature failure B15: Economizer outlet temperature failure | 1295 | 1551 | 1807 | 2063 | 2319 | 2575 | 2831 | 3087 | System Failure 2 | B0: Communication failure of fan disk 01 B1: Communication failure of fan disk 02 B2: Communication failure of fan disk 03 B3: Communication failure of fan disk 04 B4: Communication failure of fan disk 05 B5: Communication failure of fan disk 06 B6: Communication failure of fan disk 07 B7: Communication failure of fan disk 08 B8: Communication failure of fan disk 09 B9: Communication failure of fan disk 10 B10: Communication failure of fan disk 11 B11: Communication failure of fan disk 12 B12: Communication failure of fan disk 13 B13: Communication failure of fan disk 14 B14: Communication failure of fan disk 15 B15: Communication failure of fan disk 16 | 3343
Press failure 3 | B0: Fault after cooling valve B1: Fault after heating valve | 1296 | 1552 | 1808 | 2064 | 2320 | 2576 | 2832 | 3088 | System Failure 3 | B0: Fault of fan disk 01 B1: Fault of fan disk 02 B2: Fault of fan disk 03 B3: Fault of fan disk 04 B4: Fault of fan disk 05 B5: Fault of fan disk 06 B6: Fault of fan disk 07 B7: Fault of fan disk 08 B8: Fault of fan disk 09 B9: Fault of fan disk 10 B10: Fault of fan disk 11 B11: Fault of fan disk 12 B12: Fault of fan disk 13 B13: Fault of fan disk 14 B14: Fault of fan disk 15 B15: Fault of fan disk 17 | 3344
Unit failure 1 | B0: Module ambient temperature failure B1: Communication failure B2: EEPROM data error B3: Phase loss protection B4: Reverse phase protection B5: Module output temperature is too low B6: Module output temperature is too high B7: Module output temperature failure B8: Insufficient air flow B9: Fan overload protection B10: Module temperature return failure B11: Anti-icing temperature is too low B12: Anti-icing temperature failure B13: Output and return temperature difference is too large B14: Output and return temperature difference is abnormal B15: Power failure | 1298 | 1554 | 1810 | 2066 | 2322 | 2578 | 2834 | 3090 | System Failure 4 | B0: Communication failure of fan disk 17 B1: Communication failure of fan disk 18 B2: Communication failure of fan disk 19 B3: Communication failure of fan disk 20 B4: Communication failure of fan disk 21 B5: Communication failure of fan disk 22 B6: Communication failure of fan disk 23 B7: Communication failure of fan disk 24 B8: Communication failure of fan disk 25 B9: Communication failure of fan disk 26 B10: Communication failure of fan disk 27 B11: Communication failure of fan disk 28 B12: Communication failure of fan disk 29 B13: Communication failure of fan disk 30 B14: Communication failure of fan disk 31 B15: Communication failure of fan disk 32 | 3345
Unit failure 2 | B0: Communication abnormality B1: Insufficient water flow from water source B2: Condensation temperature return failure B3: Condensation temperature output failure | 1299 | 1555 | 1811 | 2067 | 2323 | 2579 | 2835 | 3091 | System Failure 5 | B0: Fan disk 17 failure B1: Fan disk 18 failure B2: Fan disk 19 failure B3: Fan disk 20 failure B4: Fan disk 21 failure B5: Fan disk 22 failure B6: Fan disk 23 failure B7: Fan disk 24 failure B8: Fan disk 25 failure B9: Fan disk 26 failure B10: Fan disk 27 failure B11: Fan disk 28 failure B12: Fan disk 29 failure B13: Fan disk 30 failure B14: Fan disk 31 failure B15: Fan disk 32 failure | 3346